## Slide 1: Storage Sizing and Placement in QuESt
Will Vining, Ujjwol Tamrakar, John Eddy
8810 ESSG Monthly Meeting
February 8, 2023

## Slide 2: Objective
An open-source python-based simulation capability
Enhances the suite of tools included with QuESt by adding a discrete event simulation for evaluating the impact of energy storage on distribution grids that incorporates
  grid physics
  reliability
  disruptions caused by extreme events
Provides a flexible architecture to support different simulations of weather, reliability, load management, energy storage, and other components
Support optimization over multiple objectives
Optimize energy storage controls as well as size and placement

## Slide 3: HELICS-based co-simulation
HELICS is used to couple several simulations
  OpenDSS grid simulation
  Grid reliability simulation
  Multiple Storage controller simulations
  Energy Management System simulation
  A threat simulation
  Multiple load simulations
Storage Controller
Storage Controller
Grid Simulation
(OpenDSS)
Storage Controller
Reliability Simulation
Energy Management System
Load Simulation
Threat model

## Slide 4: Grid Simulation
Input
  Storage power set-points
  Reliability events
  EMS Actions
Output
  Voltage at storage devices
  Storage device status (SOC, current power output/demand, etc.)
  Generator status (Current output, operating time, etc.)
  PV system status (Current generation)
  Total energy demand
OpenDSS
federate
update model
- storage power
- reliability events
- generator setpoints
- …
new output
- voltages
- storage soc
- total load
- total generation
- next update time
HELICS
reliability
storage controller
Outputs detailed information about grid operation
EMS
Notes: Advances time to the time of the next scheduled control action (or by a fixed interval if there are no pending actions)
When granted a time by HELICS
  The OpenDSS model is updated to reflect changes to the boundary variables (storage power, reliability events)
  Pending control actions are applied
  Power flow is solved
  Boundary variables are updated to reflect the new grid state
The requested time is pre-empted by
  Changes to the output of the storage controllers
  Reliability events (component failures and restorations)
  Commands from the EMS

## Slide 5: Reliability Model
  Input
  Status updates for grid components
Output
  Failure events
  Repair events
Simple probabilistic failure model
  Can be easily replaced with different models
Will respond to input from the threat federate to activate fragility models for grid components.
reliability model
federate
HELICS
grid
EMS
Component
Status from grid (e.g. generator run time)
Current threat information
Reliability events
- failure/repair events @
present time
- time of the next event/update
Threat
Notes: The reliability model observes the operation of the grid, updating probabilistic failure models and generating failure events when they are indicated by the models.

## Slide 6: Storage Controller
Inputs
  Voltage
  State of Charge
  Control messages from EMS
Outputs
  Power set-point (Real/Reactive)
  Status messages to EMS
Each storage device has its own external controller. This supports:
  Independently controlled storage devices
  Globally controlled devices (i.e. controlled by an EMS)
controller model
federate
HELICS
grid
- voltage
- state of charge
- EMS commands
- power set-point
- status
EMS

## Slide 7: EMS Design (in development)
Inputs
  Current generator output
  Current demand
  Reliability events
Outputs
  Control actions to storage controllers
  Control actions to grid model (generator setpoint changes, switch actions, etc.)
Have implemented a simple heuristic-based EMS. We are in the process of integrating an EMS that combines OPF and heuristics for better control.
  The modular architecture means using a different EMS can be a relatively simple task.
EMS
federate
update model
- grid element status
- reliability events
output
- ESS setpoints
- Generator setpoints
- Switch changes
HELICS
reliability
storage controller
Record grid state and power quality statistics
grid

## Slide 8: Quantifying Performance
The grid simulation is configured to report measurements at specific locations to a “metrics federate”
Each measured value is assigned target values (limit and objective) and an improvement type (minimize, maximize, seek-value).
The metrics federate normalizes the values it receives using a non-linear normalization curve with specific properties to support optimization over many (hundreds or thousands) of values.
Normalized metrics allow different quantities of interest to be compared directly. For example, we can examine trade offs between voltage across the grid, line loading, energy service, or any other quantity of interest.
Piecewise quadratic
Monotonically decreasing slope
Continuous

## Slide 9: Usage
The simulator is configuration-driven
  One config file specifies
    the OpenDSS model
    connected storage & PV
    Reliability model parameters
    etc.
Config files are JSON to enable human readability while keeping it easy to generate configurations from another program
A graphical UI is in development
Will enable an easy entry point for users via the QuESt tool

## Slide 10
Reliability Example

## Slide 11: Reliability Example
Generator added to the IEEE13 node system at bus 675.
  Constant 2 MW output
A Storage system is added at bus 670
  32 MWh
  1.2 MW
  50% initial SOC
  Dispatched internally by OpenDSS based on power flow at bus 632 (no controller federate)
Failure of the upstream switch connecting the generator to the rest of the grid is simulated
650
632
633
634
645
646
611
684
671
692
675
680
652
ESS
3
MWp
1.2
MW
,
32
MWh
670
2 MW
switch fails open

## Slide 12: Reliability Example - results
ESS consumes excess generation from PV system until it is fully charged
Switch fails at hour 50, disconnecting the generator
ESS picks up the lost generation
Switch is repaired 48 hours later and the ESS again re-charges from excess PV generation

## Slide 13
Metrics Example

## Slide 14: Storage for Voltage Regulation in IEEE 34 Bus Test Distribution System
Bus 814, 828, 860, 840 are “critical” - we tolerate voltage between 0.972 and 1.025 p.u.
  (arbitrary, just to demonstrate the configurability and flexibility of the metrics)
Question: What would be the size of storage required and where should it be placed?
Simulator utilized to analyze voltage regulation with PVs and explore few possible configurations of energy storage size/placements
Test Irradiance Profile
Load Demand (Measured at Substation)
Power (kw/kVAr)

## Slide 15: Analyzing the Impact of Volt-Var Function
According to IEEE 1547-2018 standard for interconnection of DERs, PV inverters need to provide grid support functions such as volt-var
Simulator has the ability to enable such inverter functions
PVs 850 and 860 are assumed to be capable of providing volt-var support
  Other PVs are considered to be older units
  Operating with MPPT injecting all the available active power
Capacitive Vars
Inductive Vars
Volt-var functions provide some level of voltage regulation – not enough on its own.

## Slide 16: Configuration 1 : Single Energy Storage Near Substation
Single energy storage placed at bus 814 for voltage regulation
Energy storage operates on a “droop-based” control strategy based on voltage measurement obtained at bus 814
  Relatively high gains were used to achieve desired voltage regulation
Droop Controller

## Slide 17: Configuration 1 – Voltages at “Critical” Buses
A 450 kW, 1500 kWh energy storage unit able to prevent overvoltage at buses 814 and 828
  These buses are near the energy storage installation
Difficult to regulate voltage at the end of the feeder (buses 840 and 860) with a single energy storage at bus 814
450 kW, 500 kVA
~1500 kWh

## Slide 18: Configuration 2: Two Energy Storage Units
Two storage units placed at buses 814 (near substation)and 840 (end of feeder)
Volt-Var function only active in PV @ 850 and 860

## Slide 19: Configuration 2- Voltage at “Critical” Buses
Voltage regulation nearly within desired limits of 0.975-1.025 p.u with two storage units
175 kW, 200kVA
~1800 kWh
250 kW, 275kVA
~750 kWh

## Slide 20: Configuration 3: Energy Storage Placed at Each “Critical” Bus
Placed 4- smaller sized distributed energy storage units at these critical buses
Droop control implemented in each energy storage based on local voltage measurements

## Slide 21: Configuration 3– Voltage on Critical Buses
Slightly better voltage regulation compared to case with configuration 2
150 kW, 175kVA
~650 kWh
150 kW, 175kVA
~350 kWh
250 kW, 275kVA
~1500 kWh
250 kW, 275kVA
~1500 kWh

## Slide 22: Voltage Metrics Based Comparison of Three Configurations
Ideally this metric should be at 1.0
  Approaches 0 as the value deviates from the target
  As the value drifts beyond the limits the metric takes negative values
Configuration 2 and 3 seem to provide nearly identical performance – the accumulated metric clearly shows better performance of configuration 3
Configuration 1
Total Accumulated Metric Value = -1,474,596
Configuration 2
Total Accumulated Metric Value = -145,942
Configuration 3
Total Accumulated Metric Value = -14,316

## Slide 23: We are looking for case studies!
Any projects that could benefit from this kind of capability/analysis – please reach out
We would like some specific and realistic use cases to develop against for the next year